# TERM SHEET

BLACKSTART SERVICE

| Company | Northern States Power Company (“Company”) |
| --- | --- |
| Blackstart Service Agreement and Associated PPA | The terms of this Blackstart Service Term Sheet shall be incorporated into a Blackstart Service Agreement, which shall be coordinated with an “Associated PPA”, which for purposes of this Term Sheet is defined as an existing power purchase agreement between Company and Seller or a new power purchase agreement entered into pursuant to Company’s 2023 800 MW Firm Dispatchable Acquisition (“Company Acquisition”). |
| Term | The Term of the Blackstart Service Agreement will match the term detailed in Seller’s application. |
| Blackstart Facility | The “Blackstart Facility” shall include the start-up energy source, blackstart generating units, load bank, and/or any other associated equipment that is necessary for Seller to provide Blackstart Service to Company. The Blackstart Facility may or may not share facilities and equipment with the Facility under the Associated PPA. |
| Blackstart Service | A facility with "Blackstart Capability" means that there is a start-up energy source located on site at the facility which is capable of starting at least one of the facility’s blackstart generating units, which in turn allows the restart of additional blackstart generating units at the facility, if applicable, without relying on the external electric power transmission system. The Blackstart Facility with Blackstart Capability will provide Blackstart Service to Company, which shall include the following (as defined below): (a) compliance with Applicable Reliability Standards; (b) compliance with Blackstart Performance Testing Requirements; (c) compliance with Blackstart Availability Requirements; (d) compliance with Company’s requirements for Re-energization Service, to be further defined in the Blackstart Service Agreement. Blackstart Service does not include any capacity, energy, ancillary, or other services. Seller will provide Blackstart Service to Company during the Term. |
| Blackstart Service Compensation | Company will pay to Seller a monthly fee for Seller’s provision of Blackstart Service to Company. In addition, Company will pay Seller for any energy produced by Seller and delivered to the Interconnection Point (as defined in Seller’s application) during performance testing and during Seller’s provision of Re-energization Service at the then current Energy Tolling Rate set forth in the Associated PPA or an amount otherwise agreed to by Company and Seller. Each time Seller fails to provide Re-energization Service when requested by Company, Seller will pay Company an amount equivalent to two (2) years of Seller’s monthly fee (monthly fee × 24), plus actual damages up to the Damage Cap (as defined below). The Company will also have the right to terminate the Blackstart Service Agreement with no further payments or obligations due to Seller. The “Damage Cap” shall be equal to the greater of: (i) two (2) years of Seller’s monthly fee (monthly fee × 24) or (ii) $1,500,000. |
| Blackstart Service Security for Performance | Prior to the successful completion of the Blackstart Commercial Operation Conditions (as detailed below), Seller shall fund and maintain security in favor of Company, at Seller’s expense, to secure Seller’s obligations to Company under the Blackstart Service Agreement. Seller shall establish and fund the security fund in the amount of $1,500,000 no later than thirty (30) days following the effective date of the Blackstart Service Agreement, in the same form(s) accepted under the Associated PPA. Without notice to Seller, Company may draw from the security fund such amounts as are necessary to recover amounts owing to Company pursuant to the Blackstart Service Agreement. For the avoidance of doubt, the security fund for the Blackstart Service Agreement shall be maintained independent of, and in addition to, the security for performance required under the Associated PPA. The Company will return to Seller the Blackstart Service Agreement security fund within five (5) business days following Seller’s successful completion of the Blackstart Commercial Operation Conditions. |
| Blackstart Commercial Operation Conditions | Seller must successfully complete an initial blackstart unit test consistent with the Restoration Plan and the Blackstart Service Agreement, which shall serve as assurance and documentation that Seller is able to begin providing Blackstart Service to Company under the terms of the Blackstart Service Agreement. The timeframe, requirements, and procedures for the initial blackstart unit test shall be mutually agreed upon by Company and Seller in the Blackstart Service Agreement. In the event Seller is unable to successfully complete the initial blackstart unit test within the timeframe agreed upon in the Blackstart Service Agreement, Company will have the right to terminate the Blackstart Service Agreement with no further obligations to Seller. Additionally, if applicable, Company may also terminate the Blackstart Service Agreement with no further obligations to Seller if Seller fails to achieve COD under the Associated PPA. For the avoidance of doubt, the Term of the Blackstart Service Agreement shall commence only after Seller has successfully completed the initial blackstart unit test and, if applicable, has successfully achieved COD under the Associated PPA. In connection with the termination of the Blackstart Service Agreement for the reasons listed above, Company may collect from Seller liquidated damages arising from such termination, in the amount of $1,500,000. These liquidated damages are separate and apart from any liquidated damages due Company as the result of the termination of the Associated PPA for the failure of the Facility to achieve COD. |
| Applicable Reliability Standards | Seller is required to comply with all Applicable Reliability Standards, which include FERC, NERC, and Reliability Coordinator requirements with respect to Blackstart Service, including, but not limited to, the “Emergency Preparedness and Operations, Standard EOP-005-3 — System Restoration from Blackstart Resources”, as they exist on the effective date of the Blackstart Service Agreement. In the event of a change in the Applicable Reliability Standards, each party will exercise commercially reasonable efforts to comply with such change. |
| Restoration Plan | “Restoration Plan” means “Blackstart [System] Restoration Plan” as defined in the NERC glossary of terms. “Blackstart Resource” is defined in the NERC glossary of terms. Upon the effective date of the Blackstart Service Agreement, Company may revise its Restoration Plan to designate the Blackstart Facility as a Blackstart Resource. |
| Blackstart Generating Unit Criteria | Each blackstart generating unit is required to meet the following criteria: - Start within the time required under the terms set forth in the Company Acquisition for that blackstart generating unit without the input of energy from the NSP Transmission System or a third-party transmission system. - Ability to continuously operate in zero droop mode. - Ability to close into a dead (de-energized) transmission bus at the Interconnection Point. - Ability to undergo multiple consecutive restart attempts. - Any other operating parameters/characteristics required under the terms set forth in the Company Acquisition and/or detailed in Seller’s application. Additionally, the D-curve (or capability curve) for the blackstart generating units that Seller submits to the Company Acquisition as part of Seller’s application shall be incorporated into the Blackstart Service Agreement. The blackstart generating units shall remain consistent with their inherent D-curve characteristics. |
| Blackstart Performance Testing Requirements | A performance test will be scheduled at Company’s discretion at least once each calendar year to verify that the Blackstart Facility is available and capable of providing Blackstart Service to Company. Company and Seller will develop mutually agreeable performance testing requirements and procedures, including cold weather testing, as part of the Blackstart Service Agreement. During the scheduled performance test, Company will provide and pay for all fuel transportation and supply costs. If Seller fails a scheduled performance test, Seller will have ten (10) days from the date of such failed performance test to conduct a successful performance test unless otherwise extended by Company. For any subsequent performance test performed following the failure of any required scheduled performance test, Seller will be responsible for all fuel transportation and supply costs. If Seller fails to conduct a successful performance test within the allotted ten (10) day period, Company’s monthly payment to Seller will be forfeited from the date of the first unsuccessful scheduled performance test until such time as a successful performance test is performed. If, after ninety (90) days, Seller has failed to conduct a successful performance test, Company will have the right to terminate the Blackstart Service Agreement with no further payments or obligations due to Seller. In connection with any such termination, Company may collect from Seller all actual damages arising from such termination, up to the Damage Cap. |
| Blackstart Availability Requirements | Seller will be able to begin providing Re-energization Service immediately and at any time when requested by Company (i.e. Blackstart Service may be initiated and provided either remotely or locally by personnel that are on-site 24/7/365). Seller will obtain by the commencement of the Term, and will thereafter maintain at the location of the start-up energy source, fuel or energy used for the operation of the start-up energy source in an amount that meets the requirements of the Company Acquisition. The start-up energy source will be available for Seller’s provision of Blackstart Service to Company at all times (with the exception being times when Seller is performing scheduled Blackstart Facility maintenance, as detailed below), and will have at least the minimum required amount of fuel or energy stored on site at all times. If Seller is unavailable to provide Blackstart Service to Company for any reason, including due to forced outages or scheduled maintenance as detailed below, for ninety (90) consecutive days or ninety (90) non-consecutive days in any 365-day period, Company may terminate the Blackstart Service Agreement with no further payments or obligations due to Seller. In connection with any such termination, Company may collect from Seller all actual damages arising from such termination, up to the Damage Cap. |
| Re-energization Service | Upon the submission of any request by Company pursuant to and consistent with the Restoration Plan, Seller shall provide Re-energization Service as defined in and in accordance with the terms of the Blackstart Service Agreement. Seller shall comply with Company’s operational and dispatch instructions for the duration of the re-energization and restoration of the NSP Transmission System in a manner pursuant to and consistent with the Restoration Plan. Company’s dispatch of the blackstart generating units shall be implemented in a manner consistent with the Restoration Plan, Good Utility Practices (as defined in Company’s Model Dispatchable PPA), Applicable Law (as defined in Company’s Model Dispatchable PPA), and the operating parameters of the Blackstart Facility as detailed in Seller’s application. |
| Blackstart Facility Maintenance | Seller will operate and maintain the Blackstart Facility in accordance with Good Utility Practices, Applicable Reliability Standards, the Associated PPA, and the Blackstart Service Agreement. Seller shall be permitted a total of seventy-two (72) hours per calendar year to conduct scheduled maintenance on the Blackstart Facility where such maintenance results in Seller being unavailable to provide Re-energization Service to Company. The annual scheduled Blackstart Facility maintenance limit of seventy-two (72) hours is independent of any scheduled maintenance hours allotted under the Associated PPA. If during a calendar year Seller exceeds the annual seventy-two (72) hour limit for scheduled Blackstart Facility maintenance, the monthly fee that Company pays to Seller for each affected month shall be prorated and adjusted downward accordingly (number of Blackstart Facility maintenance hours used in the month over the annual seventy-two (72) hour limit divided by the number of hours in the full calendar month). |
| Other Terms and Conditions | Other terms and conditions such as standard representations and warranties, regulatory approval, dispute resolution, default, termination, conditions precedent, force majeure, billing and payment, change of control, acquisition rights, assignment, insurance, notice requirements, indemnity, permits, construction and operation, communications, and any other provisions typical of this type of agreement will be agreed upon by Company and Seller in the Blackstart Service Agreement and, where applicable, will be materially similar to those in Company’s Model Dispatchable PPA. Company and Seller will also develop mutually agreeable operating procedures as part of the Blackstart Service Agreement that are consistent with the Associated PPA. |

EXHIBIT A

PHYSICAL FACILITIES AND OPERATING CHARACTERISTICS

The operating parameters and characteristics of Seller’s Blackstart Facility shall meet the requirements of the Company Acquisition. Company and Seller will incorporate the physical facilities and operating characteristics of the Blackstart Facility into an exhibit to the Blackstart Service Agreement. Such exhibit shall be consistent with Seller’s application to the Company Acquisition. The physical facilities and operating characteristics may include but are not limited to:

- Interconnection Point

- Start-up time for commencing Re-energization Service

- Start-up energy source

  - Description

  - Operating characteristics

  - Design limits

- Blackstart generating unit(s)

  - Description

  - Operating characteristics

  - Design limits

  - Size of external stabilizing loads required

  - Applicable minimum load, environmental (e.g. air emission permits), and blackstart testing restrictions

  - Minimum output restrictions at various stages of the startup sequence

  - Maximum time at minimum load

  - Maximum ramp rate

  - Minimum ramp rate

- Load bank

  - Description

  - Quantity

  - Operating characteristics

  - Design limits