EXHIBIT D.5.3

BESS Technology Specifications

Table of Contents

1.0 Battery System Specifications	2

2.0 Balance of System Specifications	7

3.0 Codes and Standards	13

This Exhibit forms an integral part of the Agreement for the [Project Name] (“Project”) between PSCO/NSP/SPS (the “Buyer”) and [Supplier Name] (the “Supplier”). The parties intend that terms appearing in initial capital letters, but not otherwise defined herein, have the meaning defined elsewhere in the Agreement. The following sections provide project specific technical specifications and standards for the Project.

# 1.0 Battery System Specifications

### Batteries

| Requirement | Description |
| --- | --- |
| General | - Buyer shall reserve the right to attend factory witness testing of battery cell and module manufacturing, and/or Battery Energy Storage System (“BESS”) balance of system integration and testing. - Batteries will have completed independently verified cycle testing prior to consideration, with guaranteed use- and calendar-based degradation comparable (within 10 %) to its peer Tier 1 battery suppliers. - Replacement modules of the same design or of a directly compatible design will be readily available from the manufacturer for a minimum of 10 years such that rack modifications are not required. |

### Thermal Management

| Requirement | Description |
| --- | --- |
| General | - Thermal management systems shall be provided to ensure equipment OEMs recommended environmental conditions are met at all times. - Thermal management equipment and systems shall be heavy-duty, industrial grade design, construction, and installation designed to provide a minimum 20-year life expectancy. - Design calculations shall include air conditioning load calculations, heating load calculations, ventilation calculations, psychometric calculations, and pressure drop calculations. |
| Design Requirements | - Cooling equipment capacity shall be sized based on end-of-life battery state-of-health (70-80%) heat dissipation coincident with maximum design ambient heat gain. - ASHRAE design requirements as specified in Project Requirements. - High efficiency filtration (80%, MERV 13) is required for HVAC units that provide a mixture of outside air and return air. For 100% recirculation style units only 30%, MERV 7 filters may be provided. - Open loop HVAC systems should be designed to operate in economizer (free cooling) mode whenever outdoor air temperature is within specified supply air temperature range. - Filter banks shall have differential pressure transmitters to monitor filter loading. - Heating calculations shall include a minimum 10% margin on capacity. Cooling calculations shall include a minimum 15% margin on sensible and latent capacity. - Thermal management equipment shall be arranged to provide for maximum efficiency of operation and to provide easy access for performing routine maintenance. - System design shall be headered such that each HVAC unit is able to provide conditioned air to the entire space within a fire partition. - Equipment redundancy shall be provided such that failure of a single unit does not result in loss of more than 50% cooling capacity. - The thermal management control system shall monitor any equipment failures resulting in loss of cooling capacity. Diminished cooling capacity shall be interlocked with the Site Controller to limit battery charging/discharging rate as necessary to avoid cooling system overload. Battery state of health should be taken into consideration when developing charge/discharge rate limit. - The thermal management systems shall interface with fire protection systems, in accordance with NFPA, other applicable codes, and the results of UL9540A. |
| Testing | - After installation, HVAC systems, if utilized, shall be functionally tested by NEBB-certified technicians to verify proper operation. - All temperature data points recorded in site data historian shall be functionally verified for proper operation. |

### Fire Detection and Suppression

| Requirement | Description |
| --- | --- |
| General | - Fire and heat detection, suppression, management, isolation, etc. shall be as needed to satisfy UL9540/9540a certification and NFPA 855 approvals. - Supplier should specify the detection method(s) integrated into the ESS enclosure. This can include but not limited to off-gas, ionizing, laser, aspiration, and/or heat-based detection systems. - System to include all components, connections, programming and equipment to provide a complete, automatic fire protection and detection system including, but not limited to, fire alarm panels / modules, detection devices, annunciation devices, suppression piping and / or agents, as needed. - Supplier is encouraged to provide optional / add-on equipment if available for the given solution. Fire suppression methods that are included or available with the proposed solution (including water-based sprinklers) should be presented with optional pricing made available to the Owner. |
| Enclosure Fire Rating | 1 hour, or per requirements of UL9540/9540, NFPA 855 or other. |
| Deflagration Panels | Deflagration systems shall be based on gas production demonstrated in UL9540A and shall meet either NFPA 68 or 69 and other local code as necessary. If NFPA 68 is used, then calculations demonstrating that the venting is adequate for the gas production measured in the UL9540A shall be provided. Similarly, if active venting per NFPA 69 is used, calculations demonstrating that the LEL is maintained below 25% shall be provided. |
| Heat / Smoke / Gas Detectors | Heat, smoke, and gas detectors shall be part of fire detection system to meet NFPA 72 and other applicable codes and standards. |
| Active Venting | Integrated into controls (with a gas specific sensor), with option to be activated manually, and with provision for natural ventilation when power is not available. |
| Clean Agent | Clean Agent systems, if utilized, shall be in accordance with the prevailing versions of NFPA 2001 and NFPA 855. A clean agent fire suppression system shall be FM200, NOVEC 1230, or equal. CO2 systems are not acceptable. |
| Fire Detection and Alarm | - Each independent fire detection system shall be designed to provide fire detection and annunciation in each of the areas affected. - Each detection control panel shall continuously monitor its detection systems for fire or trouble condition and activate the appropriate fire or trouble alarm(s). These detection and alarm functions shall be performed independently of any other plant equipment or facility. - Fire detection or fire alarms at any enclosed BESS system shall shut down the affected BESS equipment, and the PCS unit associated with the affected BESS in order to prevent possible supply of additional energy to the affected unit. - All fire system wiring installed above ground shall be installed in ridged metallic conduit. All fire system wiring shall be installed in dedicated raceways, above and below ground. |
| Addressable Fire Alarm Panels / Modules | - Local control Fire Alarm Control Panels (“FACP”) shall be furnished and installed to monitor distributed sensors and control units. - Main fire panel shall remotely transmit and annunciate all Fire, Trouble and Supervisory conditions to the facility EMS, and to a manned location as designated by Owner if required per applicable codes, standards, and local requirements - Each local control panel shall be named and identifiable and be capable of operation as a stand-alone system with its own internal secondary power via battery backup. Each remote device shall be addressable and communicate to local panel via signaling line circuit (“SLC”) circuit. - The addressable local control panel(s) shall monitor and annunciate; alarms, trouble, and supervisory signals for each of the fire protection and detection devices and systems. The panel shall be of modular construction and in accessible location. - The panel for each clean agent or pre-action sprinkler system shall also continuously monitor the systems to ensure the availability and proper operation of each system and to annunciate distinctly supervisory and trouble alarms. - Provision shall be made for extending the FACP to all planned BESS augmentation units over the lifetime of the project. - Each local control panel shall continuously monitor its associated fire suppression and/or detection system(s) for fire alarms, supervisory signals, and circuit trouble signals. - Auxiliary shutdown functions, where required, shall be designed, furnished, and installed, as a minimum, per applicable codes, standards, and local requirements. - Fire protection wiring shall include surge protection, per applicable codes, standards, and local requirements. - Upon receipt of any fire alarm signal the local alarm panel shall activate interior and exterior fire alarm horns/strobes. |
| Testing | - Vendor’s representative shall coordinate and provide final testing for fire and suppression systems. Vendor shall be responsible for costs associated with initial testing as well as costs to correct deficiencies and retest. - Vendor shall notify Owner and Authorities Having Jurisdiction (“AHJ”) (if required) at least 5 days in advance of beginning of each test. Final acceptance shall be determined by the Owner. - Documentation of the inspections and tests shall be maintained by Vendor and furnished to Owner. Defects found by these inspections and tests shall be re-inspected following repair by the same method and technique which originally identified the defect. Acceptance shall be based on identical acceptance criteria. Inspection and tests shall be in accordance with NFPA as a minimum. All parties necessary to sign off on test shall be obtained. |

# 2.0 Balance of System Specifications

### PCS

|  | Description |
| --- | --- |
| General | - The PCS shall consist of inverters, medium voltage transformers, protection, thermal management and isolation devices, close-coupled as a complete skid-mounted assembly. A combination PCS/MVT skid is also acceptable. - Contractor shall ensure the inverter and transformer design are adequate to perform the intended functions specified herein, and with utility operating requirements. - Contractor shall ensure the selected inverter is optimized to maximize power and energy generation for the environmental design requirements specified in this document. - Active power (MWac) output shall be rated in accordance with the following design conditions: - For ambient temperatures up to the Annual Cooling Design Temperature and DC voltages within the manufacturer-rated range, the inverters shall be capable of continuous operation without any de-rate in output. The manufacturer shall provide the de-rating curves for both temperature and voltage outside of the specified range. - For ambient temperatures up to the Extreme Annual Dry Bulb Temperature and DC voltages within the manufacturer-rated range, the inverters shall be capable of continuous operation at unity power factor at the POI without any de-rate in output. A gradual de-rate will be experienced in case the conditions exceed its rated DC voltage or the Annual Cooling Design Temperature. The manufacturer shall provide the de-rating curves for both temperature and voltage. - Apparent power (MVA) output shall be rated in accordance with the following design condition: - For ambient temperatures up to the Extreme Annual Dry Bulb Temperature and DC voltages within the manufacturer-rated range, inverters shall be capable of operating continuously at reactive power requirements specified in the project technical description can be maintained at the project POI, without any de-rate in output power (this may be a greater or lesser than the power factor stated, in order to overcome losses and effect in medium voltage equipment and connecting lines. - Current harmonics: in accordance with IEEE 1547, <5% THD as a system. - Inverter shall be designed to Applicable Codes, including IEEE-1547 and FCC Part 15 Sub Part B Class A standards. - Inverters shall be programmed in accordance with the requirements of the Interconnection Agreement and within the permissible range of the inverter control parameters. - Inverter shall have voltage and frequency ride-through capabilities that are in accordance with IEEE 1547, NERC Reliability Guidelines on BPS Connected Inverter-Based Resources (2018), 1547SA and in accordance with the requirements of the Interconnection Agreement. - Provisions to be provided to allow for unit removal and replacement. - Inverter shall be compatible with the SCADA System described below and should have the option for remote control of real power output. This shall be accomplished by Owner’s EMS through an on-site RTU. - Buyer shall reserve the right to attend factory witness testing of PCS. - Inverter shall provide ground alarms for the ungrounded DC bus and collection system. - Inverter shall provide DC disconnecting means required in NEC code. |

### Medium Voltage Transformers (MVT)

|  | Description |
| --- | --- |
| General | The Contractor will be responsible for the design, engineering, procurement, shipping, and installation of the MV Power transformers. Bidders shall ensure the PCS proposed is compatible with transformer specifications outlined below: - Primary voltage: as shown in project description, with elbow arrestors. - Secondary Voltage: The secondary voltage shall match the output AC voltage of the inverter(s). - High efficiency: 99% minimum at 100% of nameplate MVA rating. - Oil level, pressure/vacuum and oil temperature gauges. Oil level gauge, oil temperature and pressure instruments to be furnished with alarm contacts. - Compartmental pad-mount design, dead front, loop feed conforming to IEEE/ANSI C57.12 series standards for the type (liquid-filled or dry-type) and MVA rating of the transformer proposed. - The design shall provide minimum clear working space in front of transformers conforming to NEC Table 110-34(A). The equipment shall also conform to all applicable standards of ANSI, NEMA, UL, NEC, NESC, and IEEE C57.12. - Design life: 25 years from Substantial Completion - Ratings: 4.8 MVA or as required by the inverter configuration to equal or exceed the MVA rating of the inverter(s). Impedance 7% plus/minus 7.5% (or as required by the inverter manufacturer), cooling class = ONAN/KNAN or better. - BIL ratings: Transformer 150 kV primary (high side) accessories and bushings, 30 kV secondary (low side). High side winding shall have a BIL of 150 kV. - Temperature ratings: 65 °C average winding rise/65°C top oil rise/85°C hot spot rise. Peaking transformers may be utilized. - Ambient temperatures: Maximum 50°C, average 40°C, minimum -12°C or according to the Site. - Aluminum or copper windings. - Hook stick, load-break disconnect switch externally accessible. - Overcurrent protection via current limiting fuse/expulsion fuse pair (or VFI) and current limiting fuse up to 2.75MVA, and via provided switchgear for > 2.75 MVA. - Insulating fluid shall contain less than 1 PPM PCBs and the nameplate shall be marked accordingly. Secondary containment of transformer insulating fluid, if required, shall be provided and designed in compliance with all applicable environmental regulations. - Buyer shall reserve the right to attend factory witness testing of MV step-up transformers. - Electrical cable to the substation shall be run in an underground system. Features shall include: - Drain valve with oil and dissolved gas analysis sampling provisions on the exterior of the transformer main tank. - Automatic pressure-relief valve. - The Facility layout design to accommodate the installation of oil containment, ensuring that the insulating oil (mineral, vegetable or other) within the units doesn’t leave the site. Oil containment is required for this site and should be communicated and documented in the site SPCC Plan. - Oil level sight glass. - NEMA 2-hole ground terminal pads. - Surge arrestors shall be provided on one set of medium voltage bushings of the last transformer of each radial feeder and shall be connected by a copper ground bus to ground pads at base level. Surge arrestor class shall be dictated by the short-circuit study. Alternatively, surge protectors may be installed on the first and last transformers on the chain. - Steel divider between MV and LV compartments. - The secondary compartment door catches shall be caught at the three points and the handle shall be capable of being padlocked, and a penta-head bolt shall provide additional means of securing the door. The penta-head bolt shall be spring loaded to hold it in a retracted position unless threaded into the nut. The handle shall not be capable of being padlocked until the penta-head bolt is seated. The high voltage compartment shall be secured in place with one or more captive penta-head bolts. - Both compartment doors shall be equipped with stops for holding each door in a minimum 90° position. The stops shall be captive to prevent loss of the device and for convenience. Each door shall include a factory-installed flexible ground conductor connecting the door to the compartment. - Lifting lugs and corresponding lifting plan. |

### EMS Specifications

|  | Description |
| --- | --- |
| General | The EMS controller (computer and software) shall manage system operation and shall include, but not be limited to, the following: - Inverter controller interface - Rack and Master BMS - Controls for battery charging, discharging, balancing and SOC - System-level and component-specific alarms for out of specification conditions and malfunctions - Instantaneous and automated remote-shutdown capability - Communication interface with customer systems - HMI terminals in the battery enclosure and in the control room Management of any software versions - Cyber Security management of the BESS - Data exchange with the BESS The EMS shall provide remote and autonomous operation of the BESS. The EMS shall also be able to dispatch the BESS using a remote SCADA system, ISO and Owner dispatch. All modes of operation and setpoints shall be remotely adjustable. The controls shall: - Allow changes in settings and control modes - Have access to all the system data (at least, but not limited to, the system’s instantaneous power, current, voltage, etc.) and have ability to dispatch real and reactive power commands The EMS must provide the following data acquisition capabilities: - Ability to remotely access and monitor the data as well as have a minimum storage capacity for the duration of the proposed warranty (minimum) up to the life of the Project - Data points shall have the ability be recorded at a maximum of 1-second intervals, if required by warranty the sampling interval shall be reduced, with the capability for instantaneous collection and visualization of data |
| EMS Backup Power/UPS | Minimum 2-hour duration, based on connected equipment load, or longer as required for safety systems by the locality AHJ. |
| Site Controller | - The Site Controller shall coordinate with the PCS and BMS to perform the functions specified in this section. - The Site Controller shall interface with the Owner’s remote dispatch system. Contractor may coordinate revisions to the Owner’s existing SCADA remote interface gateway or may furnish a new gateway. The remote interface gateway shall be a SEL RTAC 3530 or equal. Communication with Owner’s remote dispatch system shall utilize DNP3 Ethernet protocol. - The Site Controller shall aggregate the operation of the individual Power Conversion Systems such that the BESS may be remotely operated as if a single asset. The Site Controller shall include a data historian function able to store a minimum of 1 month of required BESS operating data locally. The Site Controller shall include a local HMI station and shall be located in a separate control enclosure. The Site Controller hardware and application software shall be of proven technology and shall have been installed in similar applications for a minimum of one year. |
| SCADA Interface | - The BESS control system mode selection shall be possible locally via the site controller HMI or via the remote SCADA system. - The Site Controller shall locally store the data points listed at a collection interval of once per second. - The Site Controller shall aggregate the rack / string level data listed, and transmit to the remote dispatch system via SCADA RTAC at a two second intervals. - The SCADA interface must be fully capable of communicating with all required Owner energy management systems. - Full list of required SCADA control points and data points to be transmitted from/to remote dispatch to be provided during detailed design. At a minimum this interface should be planned to collect and concentrate all points necessary for O&M purposes such as transformer alarms. - The BMS shall monitor the data points listed in the following table at an interval of at least once per second. - The BMS shall monitor all data points required and store data a minimum of 24 hours of before and after any ESS alarm or event (or longer, if required by the battery OEM) for root cause / postmortem analysis and warranty claim disposition. Data points shall also be transmitted to the Site Controller / Historian for long term data storage and retrieval. System Level; Fault Status. Alarm Status. System Current. System Voltage. Power Conversion System / ESS Sub-arrays or blocks; Fault Status, from each PCS and DC:DC Converter. Alarm Status, from each PCS and DC:DC Converter. System Current, from each PCS and DC:DC Converter. System Voltage, from each PCS and DC:DC Converter. |

### Telecommunications Network

|  | Description |
| --- | --- |
| General | - Contractor’s scope includes design, equipment, and installation of a complete local area network to allow monitoring of the BESS facility from a remote location. - System and subsystems provided by Contractor shall be designed and configured for unmanned operation of the facility. - Communication connections to the remote System Operator shall connect serially via DNP 3.0 or Modbus TCP, via a plant SEL RTAC or similar. - Network media internal to equipment enclosures may be implemented via CAT 6 cables for distances up to 300 feet. - Terminations to equipment shall be made using prefabricated patch cables. CAT 6 cables exiting equipment shall first terminate on a patch panel. - Fiber installed underground on the premises shall be installed in conduit. Bends and risers extending above ground shall be metallic conduit. - Fiber installed in buildings or enclosures may be routed in inner-duct supported in instrument and control trays. - Network communications leaving the project site shall be implemented using fiber optic cable installed in HDPE or similar underground conduit following regional practices for telecommunications installations. |

# 5.0 Codes and Standards

Contractor shall design and manufacture all equipment in accordance with ANSI standards. All documents, drawings, instruction manuals and test certificates shall use English units.

All Work connected with the supply of the Project shall be in accordance with the requirements of the appropriate ANSI/IEEE standards and including any Applicable Law and a proposed Change In Law of any Governmental Authority, which proposal was in existence prior to the Execution Date but not yet made effective; but only if such proposal has been published to the public by the applicable Governmental Authority and only if those proposals are required by the applicable Governmental Authority prior to issuance of relevant permits. Where no ANSI/IEEE standard exists, the Project shall comply with recognized standards (including IEC) and design practices. If the requirements of this specification conflict with any of the above standards or practices, this specification shall apply. Based on the location of the Project, Contractor is required to determine any applicable codes pertaining to the applicable Governmental Authority.

The revisions of the following standards adopted or proposed and published to the public as of Execution Date, and required by the applicable Governmental Authority prior to issuance of relevant permits, shall apply, as applicable. All of the below will be followed based on adopted versions at Execution Date:

### General

| ANSI C2 | National Electrical Safety Code |
| --- | --- |
| NFPA 1 | Fire Code |
| IFC | International Fire Code 2021 (chapters 9 and 12) |
| IEEE 979 | Guide for Substation Fire Protection |
| NFPA 13 | Standard for the Installation of Sprinkler Systems |
| NFPA 70, CSA C22.1 | US National Electrical Code Canadian Electric Code |
| NFPA 72 | National Fire Alarm and Signaling Code |
| IBC | International Building Code |
| ASHRAE 169 | Climatic Data for Building Design Standards |
| ASCE 7 | Minimum Design Loads |
| ACI 318 | Building Code Requirements for Structural Concrete |
| ANSI S1.4-2014 | Specification for Sound Level Meters |

### BESS

| UL/CAN 9540 | Standard for Energy Storage Systems and Equipment, 2020 Edition |
| --- | --- |
| UL 9540 A | Test Method for Evaluating Thermal Runaway Fire Propagation in Battery Energy Storage Systems, 4th Edition |
| UL 1642 | Standard for Lithium Batteries (Cells) |
| UL 1741, C22.2 No. 107.1 | Standard for Inverters, Converters, Controllers and Interconnection System Equipment |
| IEEE 1547-2018 | IEEE Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces |
| NFPA 855 | Standard for the Installation of Stationary Energy Storage Systems (2020 Edition) |
| UL/CAN 1973 | Battery system |
| UL 50E, CAN/CSA-C22.2 No. 60529 | ESS Enclosure |

### Arc Flash

| IEEE 1584-2018 | AC Arc Flash Calculations Guide for Performing Arc-Flash Hazard Calculations |
| --- | --- |
| IEEE ESW 2007/NFPA 70E 2015 Annex D | DC Arc Flash Calculations IEEE Electrical Safety Workshop 2007 Maximum Power Transfer Method (implemented in software in SKM Powertools or ETAP) or another approved method |

### Transformers and Reactors

| IEEE C57 | Standards Collection: Distribution, Power, and Regulating Transformers. Note: The items below are all included where applicable by the reference above. [NEMA TR-1 Transformers, Regulators, and Reactors] |
| --- | --- |
| ASTM D6871 | Standard Specification for Natural (Vegetable Oil) Ester Fluids Used in Electrical Apparatus |
| ASTM D3487 | Standard Specification for Mineral Insulating Oil used in Electrical Apparatus. |

### Arrestors

| IEEE C62 | Standards Collection: Guides for Surge Protection |
| --- | --- |
| IEEE C62.11 | IEEE Standard for Metal-Oxide Surge Arresters for AC Power Circuits |
| NEMA LA 1 | Surge Arresters |
| IEEE C37 | Standards Collection: Circuit Breakers, Switchgear, Relays, Substations, and Fuses |
| IEEE C37.37 | IEEE Standard Loading Guide for AC High Voltage Switches (in excess of 1000 Volts) |
| NEMA SG 6 | Fuses |
| IEEE C37.46 | Specifications for Power Fuses and Fuse Disconnection Switches |
| IEEE C37.47 | Specifications for Distribution Fuse Disconnecting Switches |
| NEMA FU 1 | Low Voltage Cartridge Fuses |
| IEEE C62 | Standards Collection: Guides for Surge Protection |
| IEEE C62.11 | IEEE Standard for Metal-Oxide Surge Arresters for AC Power Circuits |
| NEMA LA 1 | Surge Arresters |
| IEEE C37 | Standards Collection: Circuit Breakers, Switchgear, Relays, Substations, and Fuses |
| IEEE C37.37 | IEEE Standard Loading Guide for AC High Voltage Switches (in excess of 1000 Volts) |
| NEMA SG 6 | Fuses |
| IEEE C37.46 | Specifications for Power Fuses and Fuse Disconnection Switches |
| IEEE C37.47 | Specifications for Distribution Fuse Disconnecting Switches |
| NEMA FU 1 | Low Voltage Cartridge Fuses |

### Protection

| IEEE C37.91 | IEEE Guide for Protecting Power Transformers |
| --- | --- |
| IEEE C37.99 | Guide for Protection of Shunt Power Capacitors |
| IEEE C37.90 | IEEE Standard for Relays and Relay Systems Associated with Electric Power Apparatus |
| IEEE C37.90.1 | IEEE Standard Surge Withstand Capability (SWC) Tests for Protective Relays and Relay Systems |
| IEEE C37.234 | Guide for Protective Relay Applications to Power System Buses |
| IEEE 242 | Recommended Practice for Protection and Coordination of Industrial and Commercial Power Systems |
| IEEE 141 | Recommended Practice for Electric Power Distribution for Industrial Plants |
| IEC 255-5 | Electric Relays. Part 5: Insulation Tests for Electric Relays |
| IEC 255-22 | Electric Relays. Part 22: Electrical Disturbance Tests for Measuring Relays and Protection Equipment |
| NERC Reliability Standards | PRC-002-2, PRC-019-2, PRC-023-2, PRC-024-2, PRC-025-2, PRC-026-1, PRC-027-1 |

### Control Equipment

| ANSI/IPC D30OG | Printed Board Dimensions and Tolerances |
| --- | --- |
| ANSI/IPC A610B | Acceptability of Printed Boards |

### Instrument Transformers

| IEEE C57.13 | IEEE Standard Requirements for Instrument Transformers |
| --- | --- |
| IEEE C57.13.2 | IEEE Standard Conformance Test Procedures for Instrument Transformers |

### Harmonics

| IEEE 1547 | IEEE Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces |
| --- | --- |
| IEEE 519 | Standard for Harmonic Control in Electric Power Systems |
| IEEE 80 | Guide for Safety in AC Substation Grounding |
| IEEE 693 | IEEE Recommended Practice for Seismic Design of Substations |

### Grounding

| IEEE 80 | Guide for Safety in AC Substation Grounding |
| --- | --- |

### Seismic

| IEEE 693 | IEEE Recommended Practice for Seismic Design of Substations. |
| --- | --- |