Exhibit K-2

BESS Performance Guarantees and Liquidated Damages

This Exhibit forms an integral part of the Agreement for the [Project Name] (“Project”) between (the “Buyer”) and [Supplier Name] (the “Supplier”). The parties intend that terms appearing in initial capital letters, but not otherwise defined herein, have the meaning defined elsewhere in the Agreement.

Testing Frequency and Costs: The Performance Test will be run at the Supplier’s expense once per Measurement Period.  The Buyer has the right to request additional testing.  No Maintenance shall be performed on the BESS between the Buyer’s request and the performance of an additional Performance Test, provided that such period shall not exceed 10 Days.  Buyer shall be responsible for all costs incurred by conducting any additional Performance Tests unless a Performance Test proves the BESS is underperforming, in which case the Supplier will be responsible for all costs, until Supplier proves the BESS meets the Performance Guarantees.

Test Records: Supplier shall record the results of each Performance Test, provide all raw data, records and results associated with each Performance Test, and shall submit a testing report detailing results and findings of the test to Buyer within eight (8) Business Days following completion of such Test.  During the performance of each Test, the BESS shall be functioning in a manner to permit Buyer to remotely monitor, observe and independently verify the performance of the BESS through the BESS’s remote monitoring and control systems.

# Performance Guarantees:

    - Guaranteed Monthly Availability = 98.0%

    - Guaranteed Power = [ MW at the POI

    - Guaranteed Energy means the Guaranteed Energy Table found below

    - Guaranteed Round-Trip Efficiency means the Guaranteed Round-Trip Efficiency Table found below

# Availability:

    - Monthly Availability: The “Monthly Availability” of the BESS for a Measurement Period is calculated by dividing the sum of the minimum of the Available Energy Measured (AEM) and the Available Power Measured (APM) of every hour of the Measurement Period by the total number of hours in the month. All Excused Event Hours are removed from the calculation. This calculation is illustrated in the following formula:

Monthly Availability =18760 * h=18760MINAEP h,APP (h) 1HM-HE * h=1HM-HEMINAEM h,APM h

    - Where the following terms have the following meanings:

Measurement Period: (i) for the first Measurement Period, the period beginning on the commercial operation date (COD) and ending on the last day of the month thereof and (ii) for each subsequent Measurement Period, each calendar month thereafter; provided, that, the last Measurement Period may be shorter than a month.

HM (h) = The number of hours in the month.

HE (h) = The number of Excused Event Hours.

AEM (h) = For any Hour (h), AEM is calculated in accordance with the following formula.

AEM=MIN1,Available Energy (h)Qualified Energy (h)

APM (h) = For any Hour (h), APM is calculated in accordance with the following formula.

APM=MIN1,Available Power (h)Qualified Power (h)

“Excused Event Hours” means, with respect to a Measurement Period, the sum of all Hours during which the BESS is operating below one hundred percent (100%) of Installed Capacity as result of Planned Outages or Force Majeure Events.

Hour = The consecutive sixty-minute period commencing on the hour, every hour, using local time at the Facility.

Available Power (h) = For any Hour (h), the lesser of (i) the average percentage of available inverters multiplied by the Qualified Power Capacity, or (ii) the Guaranteed Power Capacity.

Available Energy (h) = For any Hour (h), the lesser of (i) the average percentage of available racks multiplied by the Qualified Energy, or (ii) the Guaranteed Energy Capacity.

Qualified Power Capacity shall be assessed annually and is the lesser, in absolute value, of the Discharge Capacity Test or Charge Capacity Test within the Performance Test Plan.

Qualified Energy shall be assessed at least annually and is performed according to the “Round-Trip Efficiency and Energy Test” within the Performance Test Plan.

    - Monthly Availability Liquidated Damages: If the Monthly Availability is less than the corresponding Guaranteed Monthly Availability the following liquidated damages will apply:

“Monthly Infraction Days” shall be calculated on a monthly basis, if Monthly Availability is less than Guaranteed Monthly Availability, using the following formula: [(HM - HE) / 24] * [Guaranteed Monthly Availability – Monthly Availability]

“Monthly Availability Liquidated Damages” shall be calculated on a monthly basis using the following formula: [Monthly Infraction Days] * [([$XXX/MWh]) * (Guaranteed Energy)].  For example, if in July the BESS had the following:

  - Days in July = 31 days

    - HM (h) = 744

  - Scheduled maintenance = 8 hours

    - HE (h) = 8

  - Unscheduled maintenance = 100 hours

    - 50% partially available during Unscheduled Maintenance

  - Monthly Availability = [1 / (744 – 8)] * [(50% * 100) + (100% * 636)] = 686 / 736 = 93.2065%

  - Monthly Infraction Days = [736 / 24] * (98% - 93.2065%) = 1.47 days

  - Monthly Availability Liquidated Damages = 1.47 * [($XXX/MWh) * (800.0 MWh)] = $XXXXX

# Power:

Power shall be assessed annually using the methodology in the Performance Tests and compared to the Guaranteed Power.

    - Guaranteed Power Liquidated Damages: If the power demonstrated by the Performance Test is less than the corresponding Guaranteed Power the following liquidated damages will apply: [$XXX/MW per Day]

      - If after nine months following the Guaranteed Substantial Completion Date, Substantial Completion has still not been achieved and the power capacity demonstrated by the latest Performance Test is still less than the Project’s Guaranteed Power, the Project’s Guaranteed Power is thereby reset to the power capacity demonstrated under the most recent Performance Test.

# Energy:

Energy shall be assessed annually using the methodology in the Performance Tests and compared to the Guaranteed Energy.

    - Guaranteed Energy Capacity:

Guaranteed Energy Table
<Table provided by Bidder in Pricing Workbook>

| Year after COD | Guaranteed Energy at the end of each year (as a % of Beginning-of-Life Energy Capacity) |
| --- | --- |
| 0 | 100.0% |
| 1 | 97.5% |
| 2 | 95.0% |
| 3 | 92.5% |
| 4 | 90.0% |
| 5 | 87.5% |
| 6 | 85.0% |
| 7 | 82.5% |
| 8 | 80.0% |
| 9 | 77.5% |
| 10 | 75.0% |
| 11 | 72.5% |
| 12 | 70.0% |

    - Guaranteed Energy Liquidated Damages: If the Qualified Energy determined by the Performance Test is less than the corresponding Guaranteed Energy the following liquidated damages will apply: [$XXX/MWh per Day]

      - If after nine months following the Guaranteed Substantial Completion Date, Substantial Completion has still not been achieved and the energy capacity demonstrated by the latest Performance Test is still less than the Project’s beginning of life Guaranteed Energy (i.e., 500MWh), the Project’s Guaranteed Energy is thereby reset to the Qualified Energy demonstrated under the most recent Performance Test.

# Round-Trip Efficiency:

- Round-Trip Efficiency:

Round-Trip Efficiency =18760 * h=18760MINAEP h,APP (h) Qualified EnergyEnergy Charged

- Where the following terms have the following meanings:

Qualified Energy (kWh) = Has the meaning in Exhibit I-4.

Energy Charged (kWh) = The amount of Energy charged to the BESS over the Round-Trip Efficiency Test, measured at the POD.

- Round Trip Efficiency Test: In order to determine the Round-Trip Efficiency of the BESS, a test shall be conducted according to the Substantial Completion Test, as applicable.

- “Guaranteed Round-Trip Efficiency” means:

Guaranteed Round-Trip Efficiency Table

<Table provided by Bidder in Pricing Workbook>

| Year after COD | Guaranteed Round-Trip Efficiency (%) |
| --- | --- |
| 0 | 85.0% |
| 1 | 85.0% |
| 2 | 85.0% |
| 3 | 85.0% |
| 4 | 85.0% |
| 5 | 85.0% |
| 6 | 85.0% |
| 7 | 85.0% |
| 8 | 85.0% |
| 9 | 85.0% |
| 10 | 85.0% |
| 11 | 85.0% |
| 12 | 85.0% |

- Round-Trip Efficiency Liquidated Damages: If the Round-Trip Efficiency determined by the Round-Trip Efficiency Test is less than the corresponding Guaranteed Round-Trip Efficiency the following liquidated damages will apply:

  - $XXX per MWh multiplied by the product of charged energy and [Guaranteed Round-Trip Efficiency – Round-Trip Efficiency].

# Delivery Delay Liquidated Damages

Delay Liquidated Damages are $XXXXX per each Day that Supplier fails to achieve Delivery by the Guaranteed Delivery Date.